## Registres de configuration
| 45000 | First Register
[5 empty] | Enxxx | EN302 | EN303 | EN304 | EN305 | EN308 | EN309 | EN310 | EN319 | EN306 | EN307 | EN311 | EN312 | EN320 | EN414 | EN501 | EN502 | EN504 | EN503 | EN505 | EN500
| Modbus Register Table for Transmitters Configuration (Read / Write) |  |  |  | Name | Ambient T&H | Ambient T&H / VOC | Ambient T&H / VOC / CO2 | Tx Temp Internal Sensor | Tx Pulse | Tx Pulse (Atex) | Tx Pulse (Fludia) | Tx Contact | Tx Temp Ext PT1000 (2) | Tx Analog 4-20mA | External T&H | Tx Temp Ext PT1000 (1) | TXIO Transmitter | TxMM Transmitter | Ambient T&H | Ambient T&H E-INK | LIGHT PIR T&H | CO2 T&H AMB | WINDOW | Ambient T&H
[5 empty] | Enless Ref | TX T&H AMB 600-021 | TX VOC/T&H AMB 600-022 | TX CO2/VOC/T&H AMB 600-023 | TX TEMP INS 600-031 | TX PULSE 600-036 | TX PULSE ATEX 600-037 | TX PULSE LED 600-038 | TX CONTACT 600-039 | TX TEMP CONT2 600-232 | TX 4/20 mA 600-035 | TX T&H 600-034 | TX TEMP CONT1 600-032 | TX I/O 600-040 | TxMM 600-041 | TX T&H AMB 600-051 | TX T&H AMB E-INK 600-052 | TX LIGHT PIR T&H 600-062 | TX CO2 T&H AMB 600-053 | TX WINDOW 600-065 | TX T&H MINI 600-050
[5 empty] | Tx Type | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 17 | 18 | 19 | 20 | 22 | 25 | 26 | 27
| Register Address | Parameter | Bytes | Comment
| 45000 | Spare | 2 | Spare
| 45001 | Spare | 2 | Spare
| 45002 | Spare | 2 | Spare
1 | 45003 | DeviceID( Higher word) | 2 | Device ID HO | bar: 0 to 27
| 45004 | DeviceID( Lower word) | 2 | Device ID LO | bar: 0 to 27
| 45005 | Tx Period | 2 | Transmission Period in mins |  | Tx Period (5min) | Tx Period (15min) | Tx Period (15min) | Tx Period (5min) | Tx Period (5min) | Tx Period (5min) | Tx Period (5min) | Tx Period (5min) | Tx Period (5min) | Tx Period (5min) | Tx Period (5min) | Tx Period (5min) | Tx Period (5min) | Tx Period (5min) | Tx Period (5min) | Tx Period (5min) | Tx Period (5min) | Tx Period (5min) | Tx Period (5min) | Tx Period (5min)
| 45006 | Tx Mode | 2 | Time Windown Update bit 0 (0-Off, 1-On) RBE Enable bit 1 (0-Off, 1-On) Motion Guard Enable (not configurable) |  | TWU (bit 0) | TWU (bit 0) | TWU (bit 0) | TWU (bit 0) | TWU (bit 0) | TWU (bit 0) | TWU (bit 0) | TWU (bit 0) | TWU (bit 0) | TWU (bit 0) | TWU (bit 0) | TWU (bit 0) | TWU (bit 0) | TWU (bit 0) | TWU (bit 0) RBE (bit 1) | TWU (bit 0) RBE (bit 1) | TWU (bit 0) RBE (bit 1) | TWU (bit 0) CO2 LEDs' (bit 1) | TWU (bit 0) | TWU (bit 0) RBE (bit 1)
| 45007 | Alarm Threshold Period | 2 | Alarm Threshold Period in Secs (time before alarm is sent) |  | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | Sampling period | Sampling period | Sampling period | CO2 periodicity | zero | Sampling period
| 45008 | Tx Type | 2 | Transmitter Type |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 17 | 18 | 19 | 20 | 22 | 25 | 26 | 27
| 45009 | Alarm Setting | 2 | Alarm Setting (P1) |  | Temp Hi - P1 (0) | Temp Hi - P1 (0) | Temp Hi - P1 (0) | Temp Hi - P1 (0) | Ch1 Flow Hi - P1 (0) | Ch1 Flow Hi - P1 (0) | zero | Ch1 Input Period - P1 (0) | Temp1 Hi - P1 (0) | Analog Hi - P1 (0) | Temp1 Hi - P1 (0) | Temp1 Hi - P1 (0) | zero | zero | Temp Hi - P1(0) | Temp Hi - P1(0) | Temp Hi - P1(0) | CO2 Hi - P1(0) | Detection Sensitivity - P1(0) | Temp Hi - P1(0)
| 45010 | Alarm Setting | 2 | Alarm Setting (P2) |  | Temp Lo - P2 (0) | Temp Lo - P2 (0) | Temp Lo - P2 (0) | Temp Lo - P2 (0) | Ch1 Flow Lo - P2 (0) | Ch1 Flow Lo - P2 (0) | zero | Ch2 Input Period - P2 (0) | Temp1 Lo - P2 (0) | Analog Lo - P2 (0) | Temp1 Lo - P2 (0) | Temp1 Lo - P2 (0) | zero | zero | Temp Lo - P2(0) | Temp Lo - P2(0) | Temp Lo - P2(0) | CO2 Lo - P2(0) | zero | Temp Lo - P2(0)
| 45011 | Alarm Setting | 2 | Alarm Setting (P3) |  | Hum Hi - P3 (0) | Hum Hi - P3 (0) | Hum Hi - P3 (0) | zero | Ch1 Flow Time - P3 (0) | Ch1 Flow Time - P3 (0) | zero | zero | Temp2 Hi - P3 (0) | Loop Period - P3 (0) | Hum Hi - P3 (0) | zero | zero | zero | Hum Hi - P3 (0) | Hum Hi - P3 (0) | Hum Hi - P3 (0) | zero | zero | Hum Hi - P3 (0)
| 45012 | Alarm Setting | 2 | Alarm Setting (P4) |  | Hum Lo - P4 (0) | Hum Lo - P4 (0) | Hum Lo - P4 (0) | zero | Ch1 Leak Threshold - P4 (0) | Ch1 Leak Threshold - P4 (0) | zero | zero | Temp2 Lo - P4 (0) | zero | Hum Lo - P4 (0) | zero | zero | zero | Hum Lo - P4(0) | Hum Lo - P4(0) | Hum Lo - P4(0) | zero | zero | Hum Lo - P4(0)
| 45013 | Alarm Setting | 2 | Alarm Setting (P5) |  | zero | VOC Hi - P5 (0) | VOC Hi - P5 (0) | zero | Ch2 Flow Hi - P5 (0) | Ch2 Flow Hi - P5 (0) | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero
| 45014 | Alarm Setting | 2 | Alarm Setting (P6) |  | zero | VOC Lo - P6 (0) | VOC Lo - P6 (0) | zero | Ch2 Flow Lo - P6 (0) | Ch2 Flow Lo - P6 (0) | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero
| 45015 | Alarm Setting | 2 | Alarm Setting (P7) |  | zero | zero | CO2 Hi - P7 (0) | zero | Ch2 Flow Time - P7 (0) | Ch2 Flow Time - P7 (0) | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | PIR Sensitivity - P7(0) | zero | zero | zero
| 45016 | Alarm Setting | 2 | Alarm Setting (P8) |  | zero | zero | CO2 Lo - P8 (0) | zero | Ch2 Leak Threshold - P8 (0) | Ch2 Leak Threshold - P8 (0) | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero
| 45017 | Alarm Setting | 2 | Alarm Setting (P9) |  | zero | zero | zero | zero | OC Flow Hi - P9 (0) | OC Flow Hi - P9 (0) | OC Flow Hi - P9 (0) | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero
| 45018 | Alarm Setting | 2 | Alarm Setting (P10) |  | zero | zero | zero | zero | OC Flow Lo - P10 (0) | OC Flow Lo - P10 (0) | OC Flow Lo - P10 (0) | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero
| 45019 | Alarm Setting | 2 | Alarm Setting (P11) |  | zero | zero | zero | zero | OC Flow Time - P11 (0) | OC Flow Time - P11 (0) | OC Flow Time - P11 (0) | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero
| 45020 | Alarm Setting | 2 | Alarm Setting (P12) |  | zero | zero | zero | zero | OC Leak Threshold - P12 (0) | OC Leak Threshold - P12 (0) | OC Leak Threshold - P12 (0) | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero
| 45021 | Spare | 2 | Spare |  | zero | zero | zero | zero | Ch1 debounce count | Ch1 debounce count | Ch1 debounce count | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero
| 45022 | Spare | 2 | Spare |  | zero | zero | zero | zero | Ch2 debounce count | Ch2 debounce count | Ch2 debounce count | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero
| 45023 | Spare | 2 | Spare |  | zero | zero | zero | zero | OC debounce count | OC debounce count | OC debounce count | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero
| 45024 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45025 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45026 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45027 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45028 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45029 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45030 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45031 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45032 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45033 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45034 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45035 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45036 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45037 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45038 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45039 | Location | 2 | Device location ASCII |  | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location | Location
| 45040 | Spare | 2 | Spare |  | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero
| 45041 | Spare | 2 | Spare |  | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero
| 45042 | Spare | 2 | Spare |  | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero | zero

## Configuration du CSV
|  | EN302 | EN303 | EN304 | EN305 | EN308 | EN309 | EN310 | EN319 | EN306 | EN307 | EN311 | EN312 | EN320 | EN414 | EN501 | EN502 | EN504 | EN503 | EN505 | EN505
|  | Ambient T&H | Ambient T&H / VOC | Ambient T&H / VOC / CO2 | Tx Temp Internal Sensor | Tx Pulse | Tx Pulse (Atex) | Tx Pulse (Fludia) | Tx Contact | Tx Temp Ext PT1000 (2) | Tx Analog 4-20mA | External T&H | Tx Temp Ext PT1000 (1) | TX I/O Transmitter | TxMM Transmitter | Ambient T&H | Ambient T&H E-INK | LIGHT PIR T&H | CO2 T&H AMB | WINDOW | Ambient T&H
| CSV Ref | TX T&H AMB 600-021 | TX VOC/T&H AMB 600-022 | TX CO2/VOC/T&H AMB 600-023 | TX TEMP INS 600-031 | TX PULSE 600-036 | TX PULSE ATEX 600-037 | TX PULSE LED 600-038 | TX CONTACT 600-039 | TX TEMP CONT2 600-232 | TX 4/20 mA 600-035 | TX T&H 600-034 | TX TEMP CONT1 600-032 | TX I/O Transmitter 600-040 | TxMM Transmitter 600-041 | TX T&H AMB 600-051 | TX T&H AMB E-INK 600-052 | TX LIGHT PIR T&H 600-062 | TX CO2 T&H AMB 600-053 | TX WINDOW 600-065 | TX T&H MINI 600-050
Number on List, maximum 40 | No
Transmitter ID | TxID | Transmitter ID | Transmitter ID | Transmitter ID | Transmitter ID | Transmitter ID | Transmitter ID | Transmitter ID | Transmitter ID | Transmitter ID | Transmitter ID | Transmitter ID | Transmitter ID | Transmitter ID | Transmitter ID | Transmitter ID | Transmitter ID | Transmitter ID | Transmitter ID | Transmitter ID | Transmitter ID
Transmitter Periodicity | TxP | Periodicity (mins) | Periodicity (mins) | Periodicity (mins) | Periodicity (mins) | Periodicity (mins) | Periodicity (mins) | Periodicity (mins) | Periodicity (mins) | Periodicity (mins) | Periodicity (mins) | Periodicity (mins) | Periodicity (mins) | Periodicity (mins) | Periodicity (mins) | Periodicity (mins) | Periodicity (mins) | Periodicity (mins) | Periodicity (mins) | Periodicity (mins) | Periodicity (mins)
Tx Mode: Time Windown Update bit 0 (0-Off, 1-On) RBE Enable bit 1 (0-Off, 1-On) Motion Guard Enable (not configurable) | TxTw | TWU - bit 0 | TWU - bit 0 | TWU - bit 0 | TWU - bit 0 | TWU - bit 0 | TWU - bit 0 | TWU - bit 0 | TWU - bit 0 | TWU - bit 0 | TWU - bit 0 | TWU - bit 0 | TWU - bit 0 | TWU - bit 0 | TWU - bit 0 | TWU - bit 0 RBE - bit 1 | TWU - bit 0 RBE - bit 1 | TWU - bit 0 RBE - bit 1 | TWU - bit 0 CO2 LEDs - bit 1 | TWU - bit 0 | TWU - bit 0 RBE - bit 1
Transmitter Type | TxTy | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 17 | 18 | 19 | 20 | 22 | 25 | 26 | 27
Transmitter Location | TxLoc | Text | Text | Text | Text | Text | Text | Text | Text | Text | Text | Text | Text | Text | Text | Text | Text | Text | Text | Text | Text
Alarm Setting (0 = Disabled) | P1 | Temp Hi - P1 (0) | Temp Hi - P1 (0) | Temp Hi - P1 (0) | Temp Hi - P1 (0) | Ch1 Flow Hi - P1 (0) | Ch1 Flow Hi - P1 (0) | 0 | Ch1 Input Period - P1 (0) | Temp1 Hi - P1 (0) | Analog Hi - P1 (0) | Temp1 Hi - P1 (0) | Temp1 Hi - P1 (0) |  |  | Sensor sampling period - P1(0) | Sensor sampling period - P1(0) | Sensor sampling period - P1(0) | Sensor sampling period - P1(0) | Sensor sampling period - P1(0) | Sensor sampling period - P1(0)
Alarm Setting (0 = Disabled) | P2 | Temp Lo - P2 (0) | Temp Lo - P2 (0) | Temp Lo - P2 (0) | Temp Lo - P2 (0) | Ch1 Flow Lo - P2 (0) | Ch1 Flow Lo - P2 (0) | 0 | Ch2 Input Period - P2 (0) | Temp1 Lo - P2 (0) | Analog Lo - P2 (0) | Temp1 Lo - P2 (0) | Temp1 Lo - P2 (0) |  |  | Temp Hi - P2(0) | Temp Hi - P2(0) | Temp Hi - P2(0) | CO2 Hi - P2(0) | Detection Sensitivity - P2(0) | Temp Hi - P2(0)
Alarm Setting (0 = Disabled) | P3 | Hum Hi - P3 (0) | Hum Hi - P3 (0) | Hum Hi - P3 (0) |  | Ch1 Flow Time - P3 (0) | Ch1 Flow Time - P3 (0) | 0 |  | Temp2 Hi - P3 (0) | Loop Period - P3 (0) | Hum Hi - P3 (0) |  |  |  | Temp Lo - P3(0) | Temp Lo - P3(0) | Temp Lo - P3(0) | CO2 Lo - P3(0) |  | Temp Lo - P3(0)
Alarm Setting (0 = Disabled) | P4 | Hum Lo - P4 (0) | Hum Lo - P4 (0) | Hum Lo - P4 (0) |  | Ch1 Leak Threshold - P4 (0) | Ch1 Leak Threshold - P4 (0) | 0 |  | Temp2 Lo - P4 (0) |  | Hum Lo - P4 (0) |  |  |  | Hum Hi - P4 (0) | Hum Hi - P4 (0) | Hum Hi - P4 (0) |  |  | Hum Hi - P4 (0)
Alarm Setting (0 = Disabled) | P5 | 1: VOC Hi - P5 (0); 2: VOC Hi - P5 (0); 4: Ch2 Flow Hi - P5 (0); 5: Ch2 Flow Hi - P5 (0); 6: 0; 19: Hum Lo - P5(0); 20: Hum Lo - P5(0); 22: Hum Lo - P5(0); 27: Hum Lo - P5(0)
Alarm Setting (0 = Disabled) | P6 | 1: VOC Lo - P6 (0); 2: VOC Lo - P6 (0); 4: Ch2 Flow Lo - P6 (0); 5: Ch2 Flow Lo - P6 (0); 6: 0; 22: 0
Alarm Setting (0 = Disabled) | P7 | 2: CO2 Hi - P7 (0); 4: Ch2 Flow Time - P7 (0); 5: Ch2 Flow Time - P7 (0); 6: 0; 22: 0
Alarm Setting (0 = Disabled) | P8 | 2: CO2 Lo - P8 (0); 4: Ch2 Leak Threshold - P8 (0); 5: Ch2 Leak Threshold - P8 (0); 6: 0; 22: PIR Sensitivity - P8(0)
Alarm Setting (0 = Disabled) | P9 | 4: OC Flow Hi - P9 (0); 5: OC Flow Hi - P9 (0); 6: OC Flow Hi - P9 (0)
Alarm Setting (0 = Disabled) | P10 | 4: OC Flow Lo - P10 (0); 5: OC Flow Lo - P10 (0); 6: OC Flow Lo - P10 (0)
Alarm Setting (0 = Disabled) | P11 | 4: OC Flow Time - P11 (0); 5: OC Flow Time - P11 (0); 6: OC Flow Time - P11 (0)
Alarm Setting (0 = Disabled) | P12 | 4: OC Leak Threshold - P12 (0); 5: OC Leak Threshold - P12 (0); 6: OC Leak Threshold - P12 (0)
Alarm Setting (0 = Disabled) | P13 | 4: Ch1 Debounce (0); 5: Ch1 Debounce (0); 6: Ch1 Debounce (0)
Alarm Setting (0 = Disabled) | P14 | 4: Ch2 Debounce (0); 5: Ch2 Debounce (0); 6: Ch2 Debounce (0)
Alarm Setting (0 = Disabled) | P15 | 4: OC Debounce (0); 5: OC Debounce (0); 6: OC Debounce (0)

## Registres de statut
| Enxxx | EN302 | EN303 | EN304 | EN305 | EN308 | EN309 | EN310 | EN319 | EN306 | EN307 | EN311 | EN312 | EN320 | EN414 | EN501 | EN502 | EN504 | EN503 | EN505 | EN500
| Name | Ambient T&H | Ambient T&H / VOC | Ambient T&H / VOC / CO2 | Tx Temp Internal Sensor | Tx Pulse | Tx Pulse (Atex) | Tx Pulse (Fludia) | Tx Contact | Tx Temp Ext PT1000 (2) | Tx Analog 4-20mA | External T&H | Tx Temp Ext PT1000 (1) | TX I/O Transmitter | TxMM Transmitter | Ambient T&H | Ambient T&H E-INK | LIGHT PIR T&H | CO2 T&H AMB | WINDOW | Ambient T&H
| Enless Ref | TX T&H AMB 600-021 | TX VOC/T&H AMB 600-022 | TX CO2/VOC/T&H AMB 600-023 | TX TEMP INS 600-031 | TX PULSE 600-036 | TX PULSE ATEX 600-037 | TX PULSE LED 600-038 | TX CONTACT 600-039 | TX TEMP CONT2 600-232 | TX 4/20 mA 600-035 | TX T&H 600-034 | TX TEMP CONT1 600-032 | TX I/O Transmitter 600-040 | TxMM Transmitter 600-041 | TX T&H AMB 600-051 | TX T&H AMB E-INK 600-052 | TX LIGHT PIR T&H 600-062 | TX CO2 T&H AMB 600-053 | TX WINDOW 600-065 | TX T&H MINI 600-050
| Tx Type | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 17 | 18 | 19 | 20 | 22 | 25 | 26 | 27
Bit
Status Register (2 bytes) | 0 | Nor / Alm Msg | Nor / Alm Msg | Nor / Alm Msg | Nor / Alm Msg | Nor / Alm Msg | Nor / Alm Msg | Nor / Alm Msg | Nor / Alm Msg | Nor / Alm Msg | Nor / Alm Msg | Nor / Alm Msg | Nor / Alm Msg | Nor / Alm Msg | Nor / Alm Msg | Nor / Alm Msg | Nor / Alm Msg | Nor / Alm Msg | Nor / Alm Msg | Nor / Alm Msg | Nor / Alm Msg
| 1 | Direct / Rptr Msg | Direct / Rptr Msg | Direct / Rptr Msg | Direct / Rptr Msg | Direct / Rptr Msg | Direct / Rptr Msg | Direct / Rptr Msg | Direct / Rptr Msg | Direct / Rptr Msg | Direct / Rptr Msg | Direct / Rptr Msg | Direct / Rptr Msg | Direct / Rptr Msg | Direct / Rptr Msg | Direct / Rptr Msg | Direct / Rptr Msg | Direct / Rptr Msg | Direct / Rptr Msg | Direct / Rptr Msg | Direct / Rptr Msg
| 2 | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Volt Level ? | 0 | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level
| 3 | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Volt Level ? | 0 | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level | Batt Level
| 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ch1 DI Status | 0 | 0 | 0 | PIR Detection Status | 0 | 0 | 0
| 5 | 0 | 0 | 0 | 0 | Ch1 Status | Ch1 Status | Ch1 Status | Ch1 Status | 0 | 0 | 0 | 0 | Ch2 DI Status | 0 | 0 | 0 | 0 | 0 | Window Status | 0
| 6 | 0 | 0 | 0 | 0 | Ch2 Status | Ch2 Status | Ch2 Status | Ch2 Status | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | CO2 sample status | 0 | 0
| 7 | 0 | 0 | 0 | 0 | OC Status | OC Status | OC Status | OC Status | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0
| 8 | 0 | 0 | 0 | 0 | Ch1 debounse status | Ch1 debounse status | Ch1 debounse status | 0 | 0 | 0 | 0 | 0 | Ch1 DO Status | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 9 | 0 | 0 | 0 | 0 | Ch2 debounce status | Ch2 debounce status | Ch2 debounce status | 0 | 0 | 0 | 0 | 0 | Ch2 DO Status | 0 | RBE status | RBE status | RBE status | LED status | 0 | RBE status
| 10 | 0 | 0 | 0 | 0 | OC debounce status | OC debounce status | OC debounce status | 0 | 0 | 0 | 0 | 0 | Ch3 DO Status | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ch4 DO Status | 0 | TWU status | TWU status | TWU status | TWU status | TWU status | TWU status
| 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MotionGuard Status | MotionGuard Status | MotionGuard Status | MotionGuard Status | 0 | 0
| 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bit
Alarm Status Register (2 bytes) | 0 | Temp Hi Alm | Temp Hi Alm | Temp Hi Alm | Temp Hi Alm | Ch1 Flow Alm Hi | Ch1 Flow Alm Hi | Ch1 Flow Alm Hi | Ch1 No Change Alm | Temp1 Hi Alm | Analog Hi Alm | Temp Hi Alm | Temp1 Hi Alm | 0 | Read Reg 1 Alm | Hi Temp Alarm | Hi Temp Alarm | Hi Temp Alarm | 0 | 0 | Hi Temp Alarm
| 1 | Temp Lo Alm | Temp Lo Alm | Temp Lo Alm | Temp Lo Alm | Ch2 Flow Alm Hi | Ch2 Flow Alm Hi | Ch2 Flow Alm Hi | Ch2 No Change Alm | Temp1 Lo Alm | Analog Lo Alm | Temp Lo Alm | Temp1 Lo Alm | 0 | Read Reg 2 Alm | Lo Temp Alarm | Lo Temp Alarm | Lo Temp Alarm | 0 | 0 | Lo Temp Alarm
| 2 | Hum Hi Alm | Hum Hi Alm | Hum Hi Alm | 0 | OC Flow Alm HI | OC Flow Alm HI | OC Flow Alm HI | OC No Change Alm | Temp2 Hi Alm | 0 | Hum Hi Alm | 0 | 0 | Read Reg 3 Alm | Hi Hum Alarm | Hi Hum Alarm | Hi Hum Alarm | 0 | 0 | Hi Hum Alarm
| 3 | Hum Lo Alm | Hum Lo Alm | Hum Lo Alm | 0 | 0 | 0 | 0 | 0 | Temp2 Lo Alm | 0 | Hum Lo Alm | 0 | 0 | Read Reg 4 Alm | Lo Hum Alarm | Lo Hum Alarm | Lo Hum Alarm | 0 | 0 | Lo Hum Alarm
| 4 | 0 | VOC Hi Alm | VOC Hi Alm | 0 | Ch1 Flow Alm Lo | Ch1 Flow Alm Lo | Ch1 Flow Alm Lo | 0 | 0 | 0 | 0 | 0 | 0 | Read Reg 5 Alm | 0 | 0 | 0 | Hi CO2 Alarm | 0 | 0
| 5 | 0 | VOC lo Alm | VOC lo Alm | 0 | Ch2 Flow Alm Lo | Ch2 Flow Alm Lo | Ch2 Flow Alm Lo | 0 | 0 | 0 | 0 | 0 | 0 | Read Reg 6 Alm | 0 | 0 | 0 | Lo CO2 Alarm | 0 | 0
| 6 | 0 | 0 | CO2 Hi Alm | 0 | OC Flow Alm Lo | OC Flow Alm Lo | OC Flow Alm Lo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7 | 0 | 0 | CO2 Lo Alm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0
| 8 | 0 | 0 | 0 | 0 | Ch1 Leak Alm | Ch1 Leak Alm | Ch1 Leak Alm | 0 | 0 | 0 | 0 | 0 | 0 | Write Reg 1 Alm | MotionGuard Alarm Status | MotionGuard Alarm Status | MotionGuard Alarm Status | MotionGuard Alarm Status | 0 | 0
| 9 | 0 | 0 | 0 | 0 | Ch2 Leak Alm | Ch2 Leak Alm | Ch2 Leak Alm | 0 | 0 | 0 | 0 | 0 | 0 | Write Reg 2 Alm | 0 | 0 |  | 0 | 0 | 0
| 10 | 0 | 0 | 0 | 0 | OC Leak Alm | OC Leak Alm | OC Leak Alm | 0 | 0 | 0 | 0 | 0 | 0 | Write Reg 3 Alm | 0 | 0 |  | 0 | 0 | 0
| 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Write Reg 4 Alm | 0 | 0 |  | 0 | 0 | 0
| 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Write Reg 5 Alm | 0 | 0 |  | 0 | 0 | 0
| 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Write Reg 6 Alm | 0 | 0 |  | 0 | 0 | 0
| 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0

## Table Modbus
| 30000 | First Register
[5 empty] | EN302 | EN303 | EN304 | EN305 | EN308 | EN309 | EN310 | EN319 | EN306 | EN307 | EN311 | EN312 | EN320 | EN414 |  | EN501 | EN502 | EN504 | EN503 | EN505 | EN500
| Modbus Register Table for Transmitters (Read Only) - to be suppoorted both as Holding and Input Registers (Code 3 and 4) |  |  |  | Ambient T&H | Ambient T&H / VOC | Ambient T&H / VOC / CO2 | Tx Temp Internal Sensor | Tx Pulse | Tx Pulse (Atex) | Tx Pulse (Fludia) | Tx Contact | Tx Temp Ext PT1000 (2) | Tx Analog 4-20mA | External T&H | Tx Temp Ext PT1000 (1) | TX I/O | TxMM Transmitter |  | Ambient T&H | Ambient T&H E-INK | LIGHT PIR T&H | CO2 T&H AMB | WINDOW | Ambient T&H | Register
[5 empty] | TX T&H AMB 600-021 | TX VOC/T&H AMB 600-022 | TX CO2/VOC/T&H AMB 600-023 | TX TEMP INS 600-031 | TX PULSE 600-036 | TX PULSE ATEX 600-037 | TX PULSE LED 600-038 | TX CONTACT 600-039 | TX TEMP CONT2 600-232 | TX 4/20 mA 600-035 | TX T&H 600-034 | TX TEMP CONT1 600-032 | TX I/O Transmitter 600-040 | TxMM Transmitter 600-041 |  | TX T&H AMB 600-051 | TX T&H AMB E-INK 600-052 | TX LIGHT PIR T&H 600-062 | TX CO2 T&H AMB 600-053 | TX WINDOW 600-065 | TX T&H MINI 600-050
[5 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 18 | 19 |  | 19 | 20 | 22 | 25 | 26 | 27
| Register Address | Parameter | Bytes | Comment
| 30000 | Num_of_Dev | 2 | Number of Devices in Table | [21 empty] | 30000
| 30001 | Spare | 2 | Spare | [21 empty] | 30001
| 30002 | Spare | 2 | Spare | [21 empty] | 30002
1 | 30003 | DeviceID( Higher word) | 2 | Device ID HO | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | Device ID HO |  | Device ID Hi | Device ID Hi | Device ID Hi | Device ID Hi | Device ID Hi | Device ID Hi | 30003
| 30004 | DeviceID( Lower word) | 2 | Device ID LO | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | Device ID LO |  | Device ID Lo | Device ID Lo | Device ID Lo | Device ID Lo | Device ID Lo | Device ID Lo | 30004
| 30005 | Device Type / F/W ver | 2 | Higher Byte Type / Lower Byte Firmware version | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | HByte ( Type ) / LByte ( FW Ver ) |  | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | 30005
| 30006 | Status | 2 | Status (see bit descriptions) | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Hbyte (Slave No) / Lbyte (Slave ID) |  | Status | Status | Status | Status | Status | Status | 30006
| 30007 | Alarm Status | 2 | Alarm Status (see bit descriptions) | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status |  | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | 30007
| 30008 | Data(word1) | 2 | Data (Read Only - Read/write for TxMM) | Temperature | Temperature | Temperature | Temperature | 0 | 0 | 0 | 0 | Temperature (Ch1) | Analog Value | Temperature | Temperature (Ch1) | Ch1 DI Count HO (RO) | 0 | Data 1 (32bit) | Temperature | Temperature | Temperature | Temperature | Window Status | Temperature | 30008
| 30009 | Data(word2) | 2 | Data (Read Only - Read/write for TxMM) | Humidity | Humidity | Humidity | 0 | Ch1 Count HO | Ch1 Count HO | 0 | Ch1 Count HO | Temperature (Ch2) | 0 | Humidity | 0 | Ch1 DI Count LO | Data 1 (16bit) | Data 1 (32bit) | Humidity | Humidity | Humidity | Humidity | Window Sensor Count | Humidity | 30009
| 30010 | Data(word3) | 2 | Data (Read Only - Read/write for TxMM) | 0 | VOC | VOC | 0 | Ch1 Count LO | Ch1 Count LO | 0 | Ch1 Count LO | 0 | 0 | 0 | 0 | Ch2 DI Count HO | 0 | Data 2 (32bit) | 0 | 0 | 0 | CO2 | 0 | 0 | 30010
| 30011 | Data(word4) | 2 | Data (Read Only - Read/write for TxMM) | 0 | 0 | CO2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ch2 DI Count LO | Data 2 (16bit) | Data 2 (32bit) | 0 | 0 | Luminosity status | CO2 last sampled time | 0 | 0 | 30011
| 30012 | Data(word5) | 2 | Data (Read Only - Read/write for TxMM) | 0 | 0 | 0 | 0 | Ch2 Count HO | Ch2 Count HO | 0 | Ch2 Count HO | 0 | 0 | 0 | 0 | Ch1 DO Count | 0 | Data 3 (32bit) | 0 | 0 | PIR Detection Status | 0 | 0 | 0 | 30012
| 30013 | Data(word6) | 2 | Data (Read Only - Read/write for TxMM) | 0 | 0 | 0 | 0 | Ch2 Count LO | Ch2 Count LO | 0 | Ch2 Count LO | 0 | 0 | 0 | 0 | CH2 DO Count | Data 3 (16bit) | Data 3 (32bit) | 0 | 0 | 0 | 0 | 0 | 0 | 30013
| 30014 | Data(word7) | 2 | Data (Read Only - Read/write for TxMM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ch3 DO Count | 0 | Data 4 (32bit) | 0 | 0 | 0 | 0 | 0 | 0 | 30014
| 30015 | Data(word8) | 2 | Data (Read Only - Read/write for TxMM) | 0 | 0 | 0 | 0 | OC Count HO | OC Count HO | OC Count HO | 0 | 0 | 0 | 0 | 0 | Ch4 DO Count | Data 4 (16bit) | Data 4 (32bit) | 0 | 0 | 0 | 0 | 0 | 0 | 30015
| 30016 | Data(word9) | 2 | Data (Read Only - Read/write for TX IO and TxMM) | 0 | 0 | 0 | 0 | OC Count LO | OC Count LO | OC Count LO | 0 | 0 | 0 | 0 | 0 | Ch1 State (Coil / Reg) | 0 | Data 5 (32bit) | 0 | 0 | 0 | 0 | 0 | 0 | 30016
| 30017 | Spare | 2 | Data (Read / Write) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ch2 State (Coil / Reg) | Data 5 (16bit) | Data 5 (32bit) | 0 | 0 | 0 | 0 | 0 | 0 | 30017
| 30018 | Spare | 2 | Data (Read / Write) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ch3 State (Coil / Reg) | 0 | Data 6 (32bit) | 0 | 0 | 0 | 0 | 0 | 0 | 30018
| 30019 | Spare | 2 | Data (Read / Write) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ch4 State (Coil / Reg) | Data 6 (16bit) | Data 6 (32bit) | 0 | 0 | PIR Count | 0 | 0 | 0 | 30019
| 30020 | Tx Counter | 2 | Transmission Counter sent by Tx | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count |  | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | 30020
| 30021 | RSSI | 2 | Received RSSI value | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI |  | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | 30021
| 30022 | Timer | 2 | Time since last reading value - increments every 1 min and resets when data received | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer |  | Timer | Timer | Timer | Timer | Timer | Timer | 30022
2 | 30023 | DeviceID( Higher word) | 2 | Device ID HO | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | Device ID HO |  | Device ID Hi | Device ID Hi | Device ID Hi | Device ID Hi | Device ID Hi | Device ID Hi | 30023
| 30024 | DeviceID( Lower word) | 2 | Device ID LO | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | Device ID LO |  | Device ID Lo | Device ID Lo | Device ID Lo | Device ID Lo | Device ID Lo | Device ID Lo | 30024
| 30025 | Device Type / F/W ver | 2 | Higher Byte Type / Lower Byte Firmware version | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | HByte ( Type ) / LByte ( FW Ver ) |  | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | 30025
| 30026 | Status | 2 | Status (see bit descriptions) | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Hbyte (Slave No) / Lbyte (Slave ID) |  | Status | Status | Status | Status | Status | Status | 30026
| 30027 | Alarm Status | 2 | Alarm Status (see bit descriptions) | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status |  | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | 30027
| 30028 | Data(word1) | 2 | Data (Read Only - Read/write for TxMM) | Temperature | Temperature | Temperature | Temperature | 0 | 0 | 0 | 0 | Temperature (Ch1) | Analog Value | Temperature | Temperature (Ch1) | Ch1 DI Count HO (RO) | 0 | Data 1 (32bit) | Temperature | Temperature | Temperature | Temperature | Window Status | Temperature | 30028
| 30029 | Data(word2) | 2 | Data (Read Only - Read/write for TxMM) | Humidity | Humidity | Humidity | 0 | Ch1 Count HO | Ch1 Count HO | 0 | Ch1 Count HO | Temperature (Ch2) | 0 | Humidity | 0 | Ch1 DI Count LO | Data 1 (16bit) | Data 1 (32bit) | Humidity | Humidity | Humidity | Humidity | Window Sensor Count | Humidity | 30029
| 30030 | Data(word3) | 2 | Data (Read Only - Read/write for TxMM) | 0 | VOC | VOC | 0 | Ch1 Count LO | Ch1 Count LO | 0 | Ch1 Count LO | 0 | 0 | 0 | 0 | Ch2 DI Count HO | 0 | Data 2 (32bit) | 0 | 0 | 0 | CO2 | 0 | 0 | 30030
| 30031 | Data(word4) | 2 | Data (Read Only - Read/write for TxMM) | 0 | 0 | CO2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ch2 DI Count LO | Data 2 (16bit) | Data 2 (32bit) | 0 | 0 | Luminosity status | CO2 last sampled time | 0 | 0 | 30031
| 30032 | Data(word5) | 2 | Data (Read Only - Read/write for TxMM) | 0 | 0 | 0 | 0 | Ch2 Count HO | Ch2 Count HO | 0 | Ch2 Count HO | 0 | 0 | 0 | 0 | Ch1 DO Count | 0 | Data 3 (32bit) | 0 | 0 | PIR Detection Status | 0 | 0 | 0 | 30032
| 30033 | Data(word6) | 2 | Data (Read Only - Read/write for TxMM) | 0 | 0 | 0 | 0 | Ch2 Count LO | Ch2 Count LO | 0 | Ch2 Count LO | 0 | 0 | 0 | 0 | CH2 DO Count | Data 3 (16bit) | Data 3 (32bit) | 0 | 0 | 0 | 0 | 0 | 0 | 30033
| 30034 | Data(word7) | 2 | Data (Read Only - Read/write for TxMM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ch3 DO Count | 0 | Data 4 (32bit) | 0 | 0 | 0 | 0 | 0 | 0 | 30034
| 30035 | Data(word8) | 2 | Data (Read Only - Read/write for TxMM) | 0 | 0 | 0 | 0 | OC Count HO | OC Count HO | OC Count HO | 0 | 0 | 0 | 0 | 0 | Ch4 DO Count | Data 4 (16bit) | Data 4 (32bit) | 0 | 0 | 0 | 0 | 0 | 0 | 30035
| 30036 | Data(word9) | 2 | Data (Read Only - Read/write for TX IO and TxMM) | 0 | 0 | 0 | 0 | OC Count LO | OC Count LO | OC Count LO | 0 | 0 | 0 | 0 | 0 | Ch1 State (Coil / Reg) | 0 | Data 5 (32bit) | 0 | 0 | 0 | 0 | 0 | 0 | 30036
| 30037 | Spare | 2 | Data (Read / Write) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ch2 State (Coil / Reg) | Data 5 (16bit) | Data 5 (32bit) | 0 | 0 | 0 | 0 | 0 | 0 | 30037
| 30038 | Spare | 2 | Data (Read / Write) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ch3 State (Coil / Reg) | 0 | Data 6 (32bit) | 0 | 0 | 0 | 0 | 0 | 0 | 30038
| 30039 | Spare | 2 | Data (Read / Write) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ch4 State (Coil / Reg) | Data 6 (16bit) | Data 6 (32bit) | 0 | 0 | PIR Count | 0 | 0 | 0 | 30039
| 30040 | Tx Counter | 2 | Transmission Counter sent by Tx | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count |  | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | 30040
| 30041 | RSSI | 2 | Received RSSI value | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI |  | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | 30041
| 30042 | Timer | 2 | Time since last reading value - increments every 1 min and resets when data received | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer |  | Timer | Timer | Timer | Timer | Timer | Timer | 30042
3 | 30043 | DeviceID( Higher word) | 2 | Device ID HO | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | Device ID HO |  | Device ID Hi | Device ID Hi | Device ID Hi | Device ID Hi | Device ID Hi | Device ID Hi | 30043
| 30044 | DeviceID( Lower word) | 2 | Device ID LO | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | Device ID LO |  | Device ID Lo | Device ID Lo | Device ID Lo | Device ID Lo | Device ID Lo | Device ID Lo | 30044
| 30045 | Device Type / F/W ver | 2 | Higher Byte Type / Lower Byte Firmware version | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | HByte ( Type ) / LByte ( FW Ver ) |  | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | 30045
| 30046 | Status | 2 | Status (see bit descriptions) | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Hbyte (Slave No) / Lbyte (Slave ID) |  | Status | Status | Status | Status | Status | Status | 30046
| 30047 | Alarm Status | 2 | Alarm Status (see bit descriptions) | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status |  | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | 30047
| 30048 | Data(word1) | 2 | Data (Read Only - Read/write for TxMM) | Temperature | Temperature | Temperature | Temperature | 0 | 0 | 0 | 0 | Temperature (Ch1) | Analog Value | Temperature | Temperature (Ch1) | Ch1 DI Count HO (RO) | 0 | Data 1 (32bit) | Temperature | Temperature | Temperature | Temperature | Window Status | Temperature | 30048
| 30049 | Data(word2) | 2 | Data (Read Only - Read/write for TxMM) | Humidity | Humidity | Humidity | 0 | Ch1 Count HO | Ch1 Count HO | 0 | Ch1 Count HO | Temperature (Ch2) | 0 | Humidity | 0 | Ch1 DI Count LO | Data 1 (16bit) | Data 1 (32bit) | Humidity | Humidity | Humidity | Humidity | Window Sensor Count | Humidity | 30049
| 30050 | Data(word3) | 2 | Data (Read Only - Read/write for TxMM) | 0 | VOC | VOC | 0 | Ch1 Count LO | Ch1 Count LO | 0 | Ch1 Count LO | 0 | 0 | 0 | 0 | Ch2 DI Count HO | 0 | Data 2 (32bit) | 0 | 0 | 0 | CO2 | 0 | 0 | 30050
| 30051 | Data(word4) | 2 | Data (Read Only - Read/write for TxMM) | 0 | 0 | CO2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ch2 DI Count LO | Data 2 (16bit) | Data 2 (32bit) | 0 | 0 | Luminosity status | CO2 last sampled time | 0 | 0 | 30051
| 30052 | Data(word5) | 2 | Data (Read Only - Read/write for TxMM) | 0 | 0 | 0 | 0 | Ch2 Count HO | Ch2 Count HO | 0 | Ch2 Count HO | 0 | 0 | 0 | 0 | Ch1 DO Count | 0 | Data 3 (32bit) | 0 | 0 | PIR Detection Status | 0 | 0 | 0 | 30052
| 30053 | Data(word6) | 2 | Data (Read Only - Read/write for TxMM) | 0 | 0 | 0 | 0 | Ch2 Count LO | Ch2 Count LO | 0 | Ch2 Count LO | 0 | 0 | 0 | 0 | CH2 DO Count | Data 3 (16bit) | Data 3 (32bit) | 0 | 0 | 0 | 0 | 0 | 0 | 30053
| 30054 | Data(word7) | 2 | Data (Read Only - Read/write for TxMM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ch3 DO Count | 0 | Data 4 (32bit) | 0 | 0 | 0 | 0 | 0 | 0 | 30054
| 30055 | Data(word8) | 2 | Data (Read Only - Read/write for TxMM) | 0 | 0 | 0 | 0 | OC Count HO | OC Count HO | OC Count HO | 0 | 0 | 0 | 0 | 0 | Ch4 DO Count | Data 4 (16bit) | Data 4 (32bit) | 0 | 0 | 0 | 0 | 0 | 0 | 30055
| 30056 | Data(word9) | 2 | Data (Read Only - Read/write for TX IO and TxMM) | 0 | 0 | 0 | 0 | OC Count LO | OC Count LO | OC Count LO | 0 | 0 | 0 | 0 | 0 | Ch1 State (Coil / Reg) | 0 | Data 5 (32bit) | 0 | 0 | 0 | 0 | 0 | 0 | 30056
| 30057 | Spare | 2 | Data (Read / Write) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ch2 State (Coil / Reg) | Data 5 (16bit) | Data 5 (32bit) | 0 | 0 | 0 | 0 | 0 | 0 | 30057
| 30058 | Spare | 2 | Data (Read / Write) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ch3 State (Coil / Reg) | 0 | Data 6 (32bit) | 0 | 0 | 0 | 0 | 0 | 0 | 30058
| 30059 | Spare | 2 | Data (Read / Write) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ch4 State (Coil / Reg) | Data 6 (16bit) | Data 6 (32bit) | 0 | 0 | PIR Count | 0 | 0 | 0 | 30059
| 30060 | Tx Counter | 2 | Transmission Counter sent by Tx | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count |  | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | 30060
| 30061 | RSSI | 2 | Received RSSI value | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI |  | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | 30061
| 30062 | Timer | 2 | Time since last reading value - increments every 1 min and resets when data received | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer |  | Timer | Timer | Timer | Timer | Timer | Timer | 30062
| . |  |  | .
| . |  |  | .
| . |  |  | .
| . |  |  | .
| . |  |  | .
| . |  |  | .
.
32 | 30623 | DeviceID( Higher word) | 2 | Device ID HO | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | Device ID HO |  | Device ID Hi | Device ID Hi | Device ID Hi | Device ID Hi | Device ID Hi | Device ID Hi | 30623
| 30624 | DeviceID( Lower word) | 2 | Device ID LO | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | Device ID LO |  | Device ID Lo | Device ID Lo | Device ID Lo | Device ID Lo | Device ID Lo | Device ID Lo | 30624
| 30625 | Device Type / F/W ver | 2 | Higher Byte Type / Lower Byte Firmware version | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | HByte ( Type ) / LByte ( FW Ver ) |  | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | 30625
| 30626 | Status | 2 | Status (see bit descriptions) | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Hbyte (Slave No) / Lbyte (Slave ID) |  | Status | Status | Status | Status | Status | Status | 30626
| 30627 | Alarm Status | 2 | Alarm Status (see bit descriptions) | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status |  | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | 30627
| 30628 | Data(word1) | 2 | Data (Read Only - Read/write for TxMM) | Temperature | Temperature | Temperature | Temperature | 0 | 0 | 0 | 0 | Temperature (Ch1) | Analog Value | Temperature | Temperature (Ch1) | Ch1 DI Count HO (RO) | 0 | Data 1 (32bit) | Temperature | Temperature | Temperature | Temperature | Window Status | Temperature | 30628
| 30629 | Data(word2) | 2 | Data (Read Only - Read/write for TxMM) | Humidity | Humidity | Humidity | 0 | Ch1 Count HO | Ch1 Count HO | 0 | Ch1 Count HO | Temperature (Ch2) | 0 | Humidity | 0 | Ch1 DI Count LO | Data 1 (16bit) | Data 1 (32bit) | Humidity | Humidity | Humidity | Humidity | Window Sensor Count | Humidity | 30629
| 30630 | Data(word3) | 2 | Data (Read Only - Read/write for TxMM) | 0 | VOC | VOC | 0 | Ch1 Count LO | Ch1 Count LO | 0 | Ch1 Count LO | 0 | 0 | 0 | 0 | Ch2 DI Count HO | 0 | Data 2 (32bit) | 0 | 0 | 0 | CO2 | 0 | 0 | 30630
| 30631 | Data(word4) | 2 | Data (Read Only - Read/write for TxMM) | 0 | 0 | CO2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ch2 DI Count LO | Data 2 (16bit) | Data 2 (32bit) | 0 | 0 | Luminosity status | CO2 last sampled time | 0 | 0 | 30631
| 30632 | Data(word5) | 2 | Data (Read Only - Read/write for TxMM) | 0 | 0 | 0 | 0 | Ch2 Count HO | Ch2 Count HO | 0 | Ch2 Count HO | 0 | 0 | 0 | 0 | Ch1 DO Count | 0 | Data 3 (32bit) | 0 | 0 | PIR Detection Status | 0 | 0 | 0 | 30632
| 30633 | Data(word6) | 2 | Data (Read Only - Read/write for TxMM) | 0 | 0 | 0 | 0 | Ch2 Count LO | Ch2 Count LO | 0 | Ch2 Count LO | 0 | 0 | 0 | 0 | CH2 DO Count | Data 3 (16bit) | Data 3 (32bit) | 0 | 0 | 0 | 0 | 0 | 0 | 30633
| 30634 | Data(word7) | 2 | Data (Read Only - Read/write for TxMM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ch3 DO Count | 0 | Data 4 (32bit) | 0 | 0 | 0 | 0 | 0 | 0 | 30634
| 30635 | Data(word8) | 2 | Data (Read Only - Read/write for TxMM) | 0 | 0 | 0 | 0 | OC Count HO | OC Count HO | OC Count HO | 0 | 0 | 0 | 0 | 0 | Ch4 DO Count | Data 4 (16bit) | Data 4 (32bit) | 0 | 0 | 0 | 0 | 0 | 0 | 30635
| 30636 | Data(word9) | 2 | Data (Read Only - Read/write for TX IO and TxMM) | 0 | 0 | 0 | 0 | OC Count LO | OC Count LO | OC Count LO | 0 | 0 | 0 | 0 | 0 | Ch1 State (Coil / Reg) | 0 | Data 5 (32bit) | 0 | 0 | 0 | 0 | 0 | 0 | 30636
| 30637 | Spare | 2 | Data (Read / Write) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ch2 State (Coil / Reg) | Data 5 (16bit) | Data 5 (32bit) | 0 | 0 | 0 | 0 | 0 | 0 | 30637
| 30638 | Spare | 2 | Data (Read / Write) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ch3 State (Coil / Reg) | 0 | Data 6 (32bit) | 0 | 0 | 0 | 0 | 0 | 0 | 30638
| 30639 | Spare | 2 | Data (Read / Write) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ch4 State (Coil / Reg) | Data 6 (16bit) | Data 6 (32bit) | 0 | 0 | PIR Count | 0 | 0 | 0 | 30639
| 30640 | Tx Counter | 2 | Transmission Counter sent by Tx | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count |  | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | 30640
| 30641 | RSSI | 2 | Received RSSI value | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI |  | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | 30641
| 30642 | Timer | 2 | Time since last reading value - increments every 1 min and resets when data received | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer |  | Timer | Timer | Timer | Timer | Timer | Timer | 30642
| . |  |  | .
| . |  |  | .
| . |  |  | .
| . |  |  | .
| . |  |  | .
40 | 30783 | DeviceID( Higher word) | 2 | Device ID HO | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | Device ID HO |  | Device ID Hi | Device ID Hi | Device ID Hi | Device ID Hi | Device ID Hi | Device ID Hi | 30783
| 30784 | DeviceID( Lower word) | 2 | Device ID LO | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | ID | Device ID LO |  | Device ID Lo | Device ID Lo | Device ID Lo | Device ID Lo | Device ID Lo | Device ID Lo | 30784
| 30785 | Device Type / F/W ver | 2 | Higher Byte Type / Lower Byte Firmware version | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | HByte ( Type ) / LByte ( FW Ver ) |  | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | Type / Ver | 30785
| 30786 | Status | 2 | Status (see bit descriptions) | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Status | Hbyte (Slave No) / Lbyte (Slave ID) |  | Status | Status | Status | Status | Status | Status | 30786
| 30787 | Alarm Status | 2 | Alarm Status (see bit descriptions) | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status |  | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | Alarm Status | 30787
| 30788 | Data(word1) | 2 | Data (Read Only - Read/write for TxMM) | Temperature | Temperature | Temperature | Temperature | 0 | 0 | 0 | 0 | Temperature (Ch1) | Analog Value | Temperature | Temperature (Ch1) | Ch1 DI Count HO (RO) | 0 | Data 1 (32bit) | Temperature | Temperature | Temperature | Temperature | Window Status | Temperature | 30788
| 30789 | Data(word2) | 2 | Data (Read Only - Read/write for TxMM) | Humidity | Humidity | Humidity | 0 | Ch1 Count HO | Ch1 Count HO | 0 | Ch1 Count HO | Temperature (Ch2) | 0 | Humidity | 0 | Ch1 DI Count LO | Data 1 (16bit) | Data 1 (32bit) | Humidity | Humidity | Humidity | Humidity | Window Sensor Count | Humidity | 30789
| 30790 | Data(word3) | 2 | Data (Read Only - Read/write for TxMM) | 0 | VOC | VOC | 0 | Ch1 Count LO | Ch1 Count LO | 0 | Ch1 Count LO | 0 | 0 | 0 | 0 | Ch2 DI Count HO | 0 | Data 2 (32bit) | 0 | 0 | 0 | CO2 | 0 | 0 | 30790
| 30791 | Data(word4) | 2 | Data (Read Only - Read/write for TxMM) | 0 | 0 | CO2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ch2 DI Count LO | Data 2 (16bit) | Data 2 (32bit) | 0 | 0 | Luminosity status | CO2 last sampled time | 0 | 0 | 30791
| 30792 | Data(word5) | 2 | Data (Read Only - Read/write for TxMM) | 0 | 0 | 0 | 0 | Ch2 Count HO | Ch2 Count HO | 0 | Ch2 Count HO | 0 | 0 | 0 | 0 | Ch1 DO Count | 0 | Data 3 (32bit) | 0 | 0 | PIR Detection Status | 0 | 0 | 0 | 30792
| 30793 | Data(word6) | 2 | Data (Read Only - Read/write for TxMM) | 0 | 0 | 0 | 0 | Ch2 Count LO | Ch2 Count LO | 0 | Ch2 Count LO | 0 | 0 | 0 | 0 | CH2 DO Count | Data 3 (16bit) | Data 3 (32bit) | 0 | 0 | 0 | 0 | 0 | 0 | 30793
| 30794 | Data(word7) | 2 | Data (Read Only - Read/write for TxMM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ch3 DO Count | 0 | Data 4 (32bit) | 0 | 0 | 0 | 0 | 0 | 0 | 30794
| 30795 | Data(word8) | 2 | Data (Read Only - Read/write for TxMM) | 0 | 0 | 0 | 0 | OC Count HO | OC Count HO | OC Count HO | 0 | 0 | 0 | 0 | 0 | Ch4 DO Count | Data 4 (16bit) | Data 4 (32bit) | 0 | 0 | 0 | 0 | 0 | 0 | 30795
| 30796 | Data(word9) | 2 | Data (Read Only - Read/write for TX IO and TxMM) | 0 | 0 | 0 | 0 | OC Count LO | OC Count LO | OC Count LO | 0 | 0 | 0 | 0 | 0 | Ch1 State (Coil / Reg) | 0 | Data 5 (32bit) | 0 | 0 | 0 | 0 | 0 | 0 | 30796
| 30797 | Spare | 2 | Data (Read / Write) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ch2 State (Coil / Reg) | Data 5 (16bit) | Data 5 (32bit) | 0 | 0 | 0 | 0 | 0 | 0 | 30797
| 30798 | Spare | 2 | Data (Read / Write) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ch3 State (Coil / Reg) | 0 | Data 6 (32bit) | 0 | 0 | 0 | 0 | 0 | 0 | 30798
| 30799 | Spare | 2 | Data (Read / Write) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ch4 State (Coil / Reg) | Data 6 (16bit) | Data 6 (32bit) | 0 | 0 | PIR Count | 0 | 0 | 0 | 30799
| 30800 | Tx Counter | 2 | Transmission Counter sent by Tx | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count |  | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | Tx Count | 30800
| 30801 | RSSI | 2 | Received RSSI value | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI |  | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | Received RSSI | 30801
| 30802 | Timer | 2 | Time since last reading value - increments every 1 min and resets when data received | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer | Timer |  | Timer | Timer | Timer | Timer | Timer | Timer | 30802

## Registers Format
Label | Description | Bits | Hexadecimal | Decimal | TX T&H AMB 600-021 | TX VOC/T&H AMB 600-022 | TX CO2/VOC/T&H AMB 600-023 | TX TEMP INS 600-031 | TX PULSE 600-036 | TX PULSE ATEX 600-037 | TX PULSE LED 600-038 | TX CONTACT 600-039 | TX TEMP CONT2 600-232 | TX 4/20 mA 600-035 | TX T&H 600-034 | TX TEMP CONT1 600-032 | TX T&H AMB 600-051 | TX T&H AMB E-INK 600-052 | TX LIGHT PIR T&H 600-062 | TX CO2 T&H AMB 600-053 | TX WINDOW 600-065 | TX T&H MINI 600-050
ID (HO & LO) | Product ID | 32 bit Unsigned Integer | 0x00000000 - 0xFFFFFFFF | 0 - 4294967295 | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓
Type / Ver | HO Byte shows Product Type / LO Byte is Revision Number | 16 bit Unsigned Integer | 0x0000 - 0xFFFF | 0 - 65535 | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓
Status | To be handled Bitwise - see bit descriptions example: 0x2129 = binary 0010 0001 0010 1001 | 16 bit Unsigned Integer | 0x0000 - 0xFFFF | 0 - 65535 | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓
Alarm Status | To be handled Bitwise - see bit descriptions example: 0x2129 = binary 0010 0001 0010 1001 | 16 bit Unsigned Integer | 0x0000 - 0xFFFF | 0 - 65535 | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓
Temperature | If reading Failed, value will be 0x7FFF Temperature = Value / 10 example 0x000FD = 253 dec = 25.3 degC 0xFFD1 = 65489 = -4.7 degC ( 65536 – 65489 ) | 16 bit Signed Integer | 0x0000 - 0xFFFF | 0 - 65535 | ✓ | ✓ | ✓ | ✓ | [6 empty] | ✓ |  | ✓ | ✓ | ✓ | ✓ |  | ✓
Humidity | If reading Failed, value will be 0xFFFF Humidity = Value / 10 example: 0x0178 = 376 = 37.6% | 16 bit Unsigned Integer | 0x0000 - 0xFFFF | 0 - 65535 | ✓ | ✓ | ✓ | [7 empty] | ✓ |  | ✓ | ✓ | ✓ | ✓ |  | ✓
VOC | If reading Failed, value will be 0xFFFF VOC = value example: 0x0175 = 373 ppb | 16 bit Unsigned Integer | 0x0000 - 0xFFFF | 0 - 65535 |  | ✓ | ✓
CO2 | If reading Failed, value will be 0xFFFF CO2 = Value example: 0x0189 = 393 ppm | 16 bit Unsigned Integer | 0x0000 - 0xFFFF | 0 - 65535 |  |  | ✓ | [12 empty] | ✓
Luminosity | If reading Failed, value will be 0x7FFF Luminosity = value | 16 bit Unsigned Integer | 0x0000 - 0xFFFF | 0 - 65535 | [14 empty] | ✓
PIR | Count = Value example: 0x001B = 27 | 16 bit Unsigned Integer | 0x0000 - 0xFFFF | 0 - 65535 | [14 empty] | ✓
Window Sensor Count | Count = Value example: 0x001B = 27 | 16 bit Unsigned Integer | 0x0000 - 0xFFFF | 0 - 65535 | [16 empty] | ✓
Temperature (Ch1) | If reading Failed, value will be 0x7FFF Temperature = Value / 10 example 00FD (hex) = 253 dec = 25.3 degC FFD1 (hex) = 65489 = -4.7 degC ( 65536 – 65489 ) | 16 bit Signed Integer | 0x0000 - 0xFFFF | 0 - 65535 | [8 empty] | ✓ |  |  | ✓
Temperature (Ch2) | If reading Failed, value will be 0x7FFF Temperature = Value / 10 example 00FD (hex) = 253 dec = 25.3 degC FFD1 (hex) = 65489 = -4.7 degC ( 65536 – 65489 ) | 16 bit Signed Integer | 0x0000 - 0xFFFF | 0 - 65535 | [8 empty] | ✓
Analog Value | Current in microamps mA = Value / 1000 example: 0x1020 = 4128 = 4.128mA | 16 bit Unsigned Integer | 0x0000 - 0xFFFF | 0 - 65535 | [9 empty] | ✓
Ch1 Count HO & LO | Pulse Count = 32 bit value example: 0x0001 0203 = 66051 | 32 bit Unsigned Integer | 0x00000000 - 0xFFFFFFFF | 0 - 4294967295 |  |  |  |  | ✓ | ✓ |  | ✓
Ch2 Count HO & LO | Pulse Count = 32 bit value example: 0x0001 0203 = 66051 | 32 bit Unsigned Integer | 0x00000000 - 0xFFFFFFFF | 0 - 4294967295 |  |  |  |  | ✓ | ✓ |  | ✓
OC Count HO & LO | Pulse Count = 32 bit value example: 0x0001 0203 = 66051 | 32 bit Unsigned Integer | 0x00000000 - 0xFFFFFFFF | 0 - 4294967295 |  |  |  |  | ✓ | ✓ | ✓ | ✓
Tx Count | Count = Value example: 0x001B = 27 | 16 bit Unsigned Integer | 0x0000 - 0xFFFF | 0 - 65535 | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓
Received RSSI | RSSI = Value example: 0xFFDA = -38dbm | 16 bit Signed Integer | 0x0000 - 0xFFFF | 0 - 65535 | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓
Timer (mins) | Timer = Value example: 0x0005 = 5min | 16 bit Unsigned Integer | 0x0000 - 0xFFFF | 0 - 65535 | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓

## Voir page réseau
Device Type | Last Seen | Device ID | Data 1 | Data 2 | Data 3 | Data 4 | Data 5 | Signal Quality | RSSI | Battery
TX T&H AMB 600-021 | 5 min ago | 123456 | 20.5 ℃ | 45.5 % |  |  | alarm status | 1-4 bars | dBm | Green / Red
TX VOC/T&H AMB 600-022 | 5 min ago | 123456 | 20.5 ℃ | 45.5 % | 2000 ppb |  | alarm status | 1-4 bars | dBm | Green / Red
TX CO2/VOC/T&H AMB 600-023 | 5 min ago | 123456 | 20.5 ℃ | 45.5 % | 2000 ppb | 450 ppm | alarm status | 1-4 bars | dBm | Green / Red
TX TEMP INS 600-031 | 5 min ago | 123456 | 20.5 ℃ |  |  |  | alarm status | 1-4 bars | dBm | Green / Red
TX PULSE 600-036 | 5 min ago | 123456 | 234 | 326 | 34 | status | alarm status | 1-4 bars | dBm | Green / Red
TX PULSE ATEX 600-037 | 5 min ago | 123456 | 345 | 527 | 27 | status | alarm status | 1-4 bars | dBm | Green / Red
TX PULSE LED 600-038 | 5 min ago | 123456 | 23 | 564 | 89 | status | alarm status | 1-4 bars | dBm | Green / Red
TX CONTACT 600-039 | 5 min ago | 123456 | 68 | 74 | 22 | status | alarm status | 1-4 bars | dBm | Green / Red
TX TEMP CONT2 600-232 | 5 min ago | 123456 | 20.5 ℃ | 20.5 ℃ |  |  | alarm status | 1-4 bars | dBm | Green / Red
TX 4/20 mA 600-035 | 5 min ago | 123456 | 16.8mA |  |  |  | alarm status | 1-4 bars | dBm | Green / Red
TX T&H 600-034 | 5 min ago | 123456 | 20.5 ℃ | 45.5 % |  |  | alarm status | 1-4 bars | dBm | Green / Red
TX TEMP CONT1 600-032 | 5 min ago | 123456 | 20.5 ℃ |  |  |  | alarm status | 1-4 bars | dBm | Green / Red
TxIO 600-040 | 5 min ago | 123456 | IP1 Count | IP2 Count |  | status | alarm status | 1-4 bars | dbm | Green / Red
Tx Modbus 600-041 | 5 min ago | 123456 | Reg1 LO | Reg2 LO | Reg3 LO | Reg4LO | alarm status | 1-4 bars | dbm | Green / Red
TX T&H AMB 600-051 | 6 min ago | 123456 | 20.5 ℃ | 45.5 % |  |  |  | 1-4 bars | dbm | Green / Red
TX T&H AMB E-INK 600-052 | 7 min ago | 123456 | 20.5 ℃ | 45.5 % |  |  |  | 1-4 bars | dbm | Green / Red
TX LIGHT PIR T&H 600-062 | 9 min ago | 123456 | 20.5 ℃ | 45.5 % | Light | Presence |  | 1-4 bars | dbm | Green / Red
TX CO2 T&H AMB 600-053 | 12 min ago | 123456 | 20.5 ℃ | 45.5 % | 450 ppm |  |  | 1-4 bars | dbm | Green / Red
TX WINDOW 600-065 | 18 min ago | 123456 | Open | 10 |  |  |  | 1-4 bars | dbm | Green / Red
TX T&H MINI 600-050 | 19 min ago | 123456 | 20.5 ℃ | 45.5 % |  |  |  | 1-4 bars | dbm | Green / Red
Temperature units | 20.5 ℃
Humidity units | 45.5 %
VOC units | 2000 ppb
CO2 units | 450 ppm
4-20 units | 16.8 mA
Pulse units | decimal value
status | hex value (16 bit)
alarm status | hex value (16 bit)
Window open/close count units | decimal value
Luminosity units | Light/Dark
PIR Status units | Presence/-
window status uints | Open/Close